INVESTIGATION REPORT

Document Reference No.: SYN/GMP/DEV/2023-0136

PR No.: 84461

Date of Initiation: 26 May 2023

Table of Contents

1.	SOURCE OF NON-CONFORMITY / UNEXPECTED OUTCOME:	3

2.	DESCRIPTION OF THE NON-CONFORMITY/ UNEXPECTED OUTCOME:	3

Description:	3

2.1.	Reference Documents/Instruments/Equipment/Products/Others:	3

2.3.	A sequence of Events:	4

2.4.	Initiator Name and Department:	4

3.	INVESTIGATION TEAM:	5

4.	INVESTIGATION AND ROOT CAUSE ANALYSIS:	5

4.1.	Initial/ Preliminary Impact assessment:	5

4.1.	Immediate Actions or Correction:	6

4.2.	Historical Check:	6

4.3.	Root Cause Analysis:	6

4.4.	Details of personnel interacted:	7

4.5.	Summary of data and documents reviewed, and experiments were done (If any):	7

4.6.	Further investigation / experimental plan (If any):	7

4.7.	LIST OF ROOT CAUSES AND CONTRIBUTING FACTORS:	7

5.	IMPACT ASSESSMENT:	8

5.1.	Impact on the quality of the product:	8

The discrepancy is related to UPS drain-off and power outage in the data center and not related to the product. Hence there is no impact on the quality of the product.	8

5.2.	Impact on other products manufactured/analyzed in the same facility/lab:	8

5.3.	Impact on other batches, analysis, materials under storage, equipment, facility, systems, documents or analytical data:	8

5.4.	Impact on the quality management system, compliance, and regulatory submission documents:	8

5.5.	Impact on validated state of the product, process or analytical method(s) or on stability status:	8

5.6.	Impact on Preventive Maintenance, calibration, or qualification status of the equipment, utility or facility:	8

6.	CORRECTIVE AND PREVENTIVE ACTIONS:	9

7.	CONCLUSION:	9

9.	ABBREVIATIONS:	11

# SOURCE OF NON-CONFORMITY / UNEXPECTED OUTCOME:

| Source of Non-Conformity | Category of Non-Conformity (Critical/ Major/ Minor) | Document Reference Number |
| --- | --- | --- |
| Deviation | Major | Document Reference No.: SYN/GMP/DEV/2023-0136 PR No.: 84461 |

# DESCRIPTION OF THE NON-CONFORMITY/ UNEXPECTED OUTCOME:

# Description:

During review of study data Swetha Malgatti (Emp. id. 10026479) observed that Data of study U-22107 were not available in the SYNGNAS shared folder drive analysed (\\syngnas\Clinical_Development\BAL-II\SMP\Source Data) on BA-LE-116. The issue has been reported by Swetha Malgatti to Kishore Yadav (Emp. id. 10029030), Abhijit Dubey (Emp. id. 10009973) and Sendhil Kumar (Emp. id. 10029036) on 17 May 2023.

Desired state: The user Swetha (Emp. id. 10026479) shall be able to access the Study data for study no. U-22107 as per Section 6.2.8 of SOP-GLP-BAL-II-0051 version 5.0, Operation, Calibration and Maintenance of Microplate/ Cuvette Reader - Molecular Devices and Associated Software. Refer Attachment- 01

However, she was not able to access the study data. Hence, the deviation was initiated.

# A sequence of Events:

Table 1: Sequence of events details

| Date | Time | Event |
| --- | --- | --- |
| 17 May 2023 | NA | During review, Swetha Malgatti (Emp. id. 10026479) observed that Data of study U-22107 were not available in the SYNGNAS shared folder drive. |
| 17 May 2023 | NA | The issue was reported by Swetha Malgatti to Kishore Yadav (Emp. id. 10029030), Abhijit Dubey (Emp. id. 10009973) and Sendhil Kumar (Emp. id. 10029036) over a call. |
| 17 May 2023 | NA | Sendhil Kumar (Emp. id. 10029036) initiated verification for the Syngnas folder (\\syngnas\Clinical_Development\BAL-II\SMP\Source Data) for data availability. He didn’t find the data in the folder. |
| 23 May 2023 to 26 May 2023 | NA | Sendhil Kumar (Emp. id. 10029036) along with Data Centre Vendor and Devendra Chougale(10011845) observed power issue in storage rack-3 of Data centre. |
| 26 May 2023 | NA | Sendhil Kumar (Emp. id. 10029036) informed to Tejas Patel (10026139) raised deviation. |
| 26 May 2023 | 17:52 | Tejas Patel (10026139) raised deviation in Trackwise for Investigation. |

# Initiator Name and Department:

Table 2: Details of initiator

| Deviation number | Initiated by | Date of initiation | Department |
| --- | --- | --- | --- |
| SYN/GMP/DEV/2023-0136 PR No.: 84461 | Tejas Patel (10026139) | 26 May 2023 | IT |

Delay Justification: The IT team and user department verify the availability of data. It took longer time to conclude that data were unavailable rather than access issue. Hence, there was a delay in initiating deviation.

# INVESTIGATION TEAM:

Table-03: Investigation Team

| Name | Designation | Emp. ID | Department |
| --- | --- | --- | --- |
| Shashi Kumar D | Executive | 10024045 | EAM |
| Devendra Chougale | Deputy Manager | 10011845 | EAM |
| Abhijit Dubey | Manager | 10009973 | IT |
| Tejas Patel | Deputy Manager | 10026139 | IT |
| Ranjith Kumar | Deputy Manager | 10023059 | IT |
| # Kumaravel Gnanasekaran | Associate Manager | 10009517 | BRL |
| Aditya Radhakrishnan | Junior Manager | 10009527 | HPU |
| Mahathevan Pillai | Associate Manager | 10009499 | Clinical Development CLAB |

# INVESTIGATION AND ROOT CAUSE ANALYSIS:

# Initial/ Preliminary Impact assessment:

- Swetha Malgatti (Emp. id. 10026479) observed that Data of study U-22107 were not available in the Syngnas shared folder drive. She informed to Kishore Yadav (Emp. id. 10029030), Abhijit Dubey (Emp. id. 10009973) and Sendhil Kumar (Emp. id. 10029036) on 17 May 2023 about the data unavailability in Syngnas share folder.

- Sendhil Kumar (Emp. id. 10029036) from IT department, along with Data Centre vendor and Devendra Chougale from EAM found there was a power outage on 15 May 2023 at Data Center as UPS was failed. Due to power failure, storage drive in Data centre got impacted which led to data unavailability in Syngnas folder.

# Immediate Actions or Correction:

As an Immediate action, the Data restoration from Commvault was verified on 26 May 2023, from the previous backup jobs of 25 May 2023. However, in the backup also data were not available as data didn’t stored in Syngnas.

The S18-UPS-05 battery alarm issue (Battery end of discharge) was observed at 11:53:39 on 15 May 2023  by Shashi Kumar (Emp. ID: 10024045) which led to Power fail. The issue was addressed on 16 May 2023 by Shashi Kumar (Refer Attachment-02 Battery Alarm report). The battery cable was changed by him on 16 May 2023 as per UPS vendor recommendation.

Historical Check:

The history of deviations was verified from trackwise for one year i.e., 25 May 2022 to 25 May 2023 and no similar deviation was found.

# Root Cause Analysis:

The Root cause analysis was done as per Why-Why Analysis for Data Unavailability in Syngnas. Below is the outcome of Why-Why analysis.

Problem Statement: Data of study U-22107 were not available in the Syngnas shared folder drive.

Why data was not available in the Syngnas shared folder drive.?

Ans: Sendhil Kumar (Emp. id. 10029036) initiated verification for the Syngnas folder (\\syngnas\Clinical_Development\BAL-II\SMP\Source Data) for data availability. He didn’t find the data in the folder. Devendra from EAM identified power failure in UPS-1 connected to Data center.

Why Power loss happened in Data center?

Ans: Due to Raw power failure on date 15 May 2023 & UPS was not able to provide backup power to Data center.

Why UPS was not able to provide backup power for Data center?

Ans. Battery terminal cable was damaged due to battery terminal leakage, which led to error in battery of UPS: S18-UPS-05. So, UPS failed to provide power backup. Refer Attachment-03 for vendor service report

Why the Redundant UPS S18-UPS-06 did not supply power during S18-UPS-05 failure?

Ans: There were two UPS i.e., S18-UPS-05 & S18-UPS-06 which provided as a redundancy for the data centre for all the racks. During verification by HPE vendor along with Sendhil kumar on 01 Jun 2023, it was identified that both Main & redundancy backup power was provided from S18-UPS-05 only to the Rack-03 Cage -09 and S18-UPS-06 was not connected. Hence during the failure of S18-UPS-05 other UPS back up did not provide power to the rack-03 Cage-09.

Power Distribution Diagram.

Inference: From the Above Why-Why analysis, it was concluded that as redundant S18-UPS-06 was not connected to rack-03 Cage-09 which had storage drive (Syngnas) & S18-UPS-05 got battery error and lead to power outage to the Rack-03 Cage-09. Hence, The power interruption impacted the data in Syngnas storage.

Procedure Evaluation:

- The SOP: SOP-GMP-EAM-0011 was verified for Preventive Maintenance of UPS. There was no ambiguity in SOP for PM of UPS. The Devendra Chougale from EAM Verified UPS (S18-UPS-05) preventive maintenance status and found that preventive maintenance was done on 27 Feb 2023 (Refer Attachment-04: PM checklist).

As a part of SOP: SOP-GMP-EAM-0011, Battery impedance test report of S18-UPS-05 and S18-UPS-06 has been verified and found satisfactory. (Refer Attachment-05: Battery impedance test report).

- The SOP: GP-CQA-IT-0033 Data Centre and Server Monitoring was verified and found that SOP clearly states Data centre shall have dual UPS connection. No ambiguity found in SOP. However, SOP was not having information about dual UPS power supply verification if any modification in racks are done.

Inference: The SOP-GMP-EAM-0011 was verified about PM activity of UPS. The procedure was found satisfactory. The GP-CQA-IT-0033 was verified and found the SOP was not having the details about dual power verification whenever modification is done in Data centre Racks.

Sendhil Kumar, Ranjith Kumar consulted Data Centre Vendor (HPE) to identify, how power supply interrupted data in Syngnas? The HPE Vendor identified, any Data generated during the power failure (Approx. 11:53-12:06, 15 May 2023) will not get stored in Syngnas storage drive. Further the power interruption caused the bad sectors in storage drive which affected the other data as well which were generated in the Syngnas. The Detailed Impact assessment shall be performed to identify other study data. Refer Attachment-06

Inference: The power interruption led to creation of bad sectors in Syngnas storage, which affected other data.

# Details of personnel interacted:

Table-04: Details of personnel who interacted

| Name | Designation | Department / Role | Employee ID |
| --- | --- | --- | --- |
|  | Executive | EAM |  |

# Summary of data and documents reviewed, and experiments were done (If any):

As part of the investigation, the following documents were reviewed:

- UPS Failure report

- Data centre Power Distribution Schematic drawing

- SOP-GLP-BAL-II-0051 V5.0 version 5.0, Operation, Calibration and Maintenance of Microplate/ Cuvette Reader - Molecular Devices and Associated Software.

- S18-UPS-05 Preventive maintenance checklist

- SOP: GP-CQA-IT-0033: Server and Data Centre Monitoring

- SOP-GMP-EAM-0011 Preventive Maintenance Procedure of CRV & UPS System

# Further investigation / experimental plan (If any):

Not Applicable as no further investigation is required.

# LIST OF ROOT CAUSES AND CONTRIBUTING FACTORS:

Table-05: List of root cause and contributing factors

| Type (Definitive root cause/ Most Probable root cause / Contributing factor) | Cause Description |
| --- | --- |
| Definitive root cause | The Root cause for study data unavailability was as a power failure in UPS in Rack 3 Cage-09 of Data Centre, so the data did not get save in the data center. |
| Contributing factor | Both Main & redundancy backup power was provided from S18-UPS-05 only to the Rack-03 Cage -09 and S18-UPS-06 was not connected. Hence during the failure of S18-UPS-05 other UPS back up did not provide power to the rack-03 Cage-09. |

# IMPACT ASSESSMENT:

# Impact on the quality of the product:

# The deviation is related to unavailability of Bioanalytical Data in Syngnas. Hence, there is no impact on quality of product.

# Impact on other products manufactured/analysed in the same facility/lab:

# The study data for U-22107 in BAL-II functions were not available. There is an impact on the analytical study data due to power failure at Data Centre Rack 3.

The data from below systems were directly mapped in Syngnas from BAL-II.

| Sr. no. | Department | Instrument ID | Application/ Instrument Name | Application Version |
| --- | --- | --- | --- | --- |
| 1 | BAL-II | BA-LE-143 | MSD Discovery Workbench | 4.0.11 |
| 2 | BAL-II | BA-LE-179 | MSD Discovery Workbench | 4.0.12 |
| 3 | BAL-II | BA-LE-116 | SoftMax Pro GxP and GxP Admin | 5.4.1 and 2.1.1 |
| 4 | BAL-II | BA-LE-033 | SoftMax Pro GxP and GxP Admin | 5.4.1 and 2.1.1 |
| 5 | BAL-II | BA-LE-170 | SoftMax Pro GxP and GxP Admin | 5.4.1 and 2.1.1 |
| 6 | BAL-II | BA-LE-008 | BioTek Gen5 secure | 3.09 |
| 7 | BAL-II | BA-LE-066 | BioTek Gen5 secure | 3.09 |

Below are the details of the affected raw data in studies in BAL-II.

| Sr. no. | Batch Details | Instrument name | Instrument ID | Analytical data details | Analyst name |
| --- | --- | --- | --- | --- | --- |
| 1. | 069/U-19014/SA | SMP | BA-LE-116 | Sample analysis | Benila Roy |
| 2. | 021/U-22283/MD | SMP | BA-LE-116 | Dilution Linearity | Pradeep |
| 3. | 070/U-19014/SA | SMP | BA-LE-116 | Sample analysis | Benila Roy |
| 4. | 071/U-19014/SA | SMP | BA-LE-116 | Sample analysis | Benila Roy |
| 5. | 042/U-19142/SA/RSA/CRA | SMP | BA-LE-116 | Sample analysis (RSA-5, CRA-1) | Vijay M |
| 6. | 005/U-21009/SA | SMP | BA-LE-116 | Sample analysis (1 sample) | Arushi |
| 7. | 022/U-22283/MD | SMP | BA-LE-033 | Dilution Linearity | Pradeep |
| 8. | 100/U-20302/MD | SMP | BA-LE-116 | STD/QC Manual Recovery Check in Bulk Pool | Asha Vijayan |

# Impact on other batches, analysis, materials under storage, equipment, facility, systems, documents or analytical data:

The Impact was verified for other studies. During Impact assessment it was observed that other study data were impacted due to interruption in power supply at Data centre rack 3. Below is the impact details for other departments:

Bioanalytical research lab:

To verify the impact at Bioanalytical research lab data, the separate OU specific deviation was initiated i.e.PR# 85823.

The Impact was verified for the Bioanalytical research lab data stored at Syngas and observed that the primary data is not lost.  Hence, there is no direct impact on analytical data or facility or material. However, the data saved during 15 May 2023 to 17 May 2023 were not available for Studies numbers: MV-142-22-Zolpidem, SYNCD-079-22-Tofacitinib, DOXA-TFR-1004, and DOXA-TFR-1005 and same were regenerated from Primary data from Instruments.

For these studies, the chromatographic data were regenerated again from primary LC-MS data from the local computer. The hard copies were scanned and placed for the documents like ISTD variation excels, study sample analysis plans, etc.

HPU: 
To verify the impact at Human Pharmacological Unit data, the separate OU specific deviation was initiated i.e.PR# 87230. During Impact assessment it was identified that no data were impacted due to Power shutdown at Data centre.

Clinical Development CLAB:

To verify the impact at Clinical Development CLAB data, the separate OU specific deviation was initiated i.e.PR 85941. During Impact assessment it was identified that no data were impacted due to Power shutdown at Data centre at Clinical Development CLAB.

# Impact on the quality management system, compliance, and regulatory submission documents:

The deviation was initiated for the discrepancy of a power outage that occurred at the data center. The discrepancy is not related to any change in the quality management system. However there is an impact on the compliance, and regulatory submission study documents.

# Impact on validated state of the product, process or analytical method(s) or on stability status:

The discrepancy is related to the power outage in the data center and not related to any change in the validated state of the product, process, or analytical method(s); hence there is no impact.

# Impact on Preventive Maintenance, calibration, or qualification status of the equipment, utility or facility:

As part of initial impact assessment, the preventive maintenance checklist was verified and found that PM of UPS was done as per schedule on 27 Feb 2023. Hence there is no impact on the Preventive maintenance, calibration or Qualification status of the equipment, utility, or facility.

# CORRECTIVE AND PREVENTIVE ACTIONS:

Table-07: Corrective Actions and preventive action.

| Sl. No. | Correction | Responsibility (Department) | Target Timeline |
| --- | --- | --- | --- |
| 1. | UPS: S18-UPS-05 battery alarm issue was checked by Mr. Shashi Kumar (Emp. ID: 10024045) and the battery cable was changed by him. | EAM | Completed on 16 May 2023. |
| Sl. No. | Corrective Action | Responsibility (Department) | Target Timeline |
| 1 | Power connections were verified and corrected in Rack-03 for availability of both power source i.e., S18-UPS-05 & S18-UPS-06. | IT & EAM | Completed on 01 Jun 2023 |
| 2. | The Reanalysis of samples was performed for impacted studies. | BAL-II | Completed on 05 Jul 2023 |
| 3 | The BRL chromatographic data were regenerated again from primary LC-MS data from the local computer. The hard copies were scanned and placed for some documents like ISTD variation excels, study sample analysis plans, etc. | BRL | Completed on 30 Jun 2023 |
| 4 | All the data from SYNGNAS to a new unified storage SYNGFMS were migrated to continue the business by IT Team. | IT | Completed on 17 Jun 2023 |

| Sl. No. | Preventive action | Responsibility (Department) | Target Timeline |
| --- | --- | --- | --- |
| 1 | The Power connection was verified for all the 5 Racks of Data center. No issues were identified during verification in Rack-01, Rack-02, Rack-03, Rack-04 and Rack-05 by taking downtime. Refer Attached Work order for details. Attachment-07 | IT & EAM | Completed on 16 Jul 2023. |
| 2. | The SOP: GP-CQA-IT-0033 ‘Server and Data center Monitoring’ shall be revised to provide clarity - Any changes in the UPS power source EAM shall ensure both the sources of power are distributed in all the racks. - Whenever there is a modification in Data Center Racks, the dual UPS connection shall be ensured by IT. | IT | 30 Nov 2023 |

# CONCLUSION:

# The Deviation was initiated for unavailability of study data for U-22107.

The Root cause was identified as a S18-UPS-05 battery issue which led to Power shutdown at Rack-03 Cage-09 at Data centre for Data availability. The Contributing factor was observed as an incorrect power connection to S18-UPS-06.

The Impact assessment was performed for power failure and observed that Study data of 8 studies were not available at BAL-II.

As a correction, battery cable was changed for S18-UPS-05.

As a Corrective action, the Power connections were verified and corrected for S18-UPS-05 and S18-UPS-06. Reanalysis was performed for affected study data of BAL-II. The Study data of BRL were regenerated from Raw data available in Instrument. The data from SYNGNAS were migrated to SYNGFMS.

As a Preventive action, the Power connections were verified for Racks of Data Centre. The SOP:      GP-CQA-IT-0033 ‘Server and Data centre Monitoring’ shall be revised to provide clarity about UPS connections

- ATTACHMENTS:

| Attachment no. | Details |
| --- | --- |
|  | SOP-GLP-BAL-II-0051. |
|  | S18-UPS-05 Alarm report. |
|  | Vertiv Service report. |
|  | S18 UPS 05 PM Checklist. |
|  | Battery Impedance report |
|  | Investigation by HPE Vendor. |
|  | Work order |

# ABBREVIATIONS:

| No. | : Number |
| --- | --- |
| SYN | : Syngene |
| DEV | : Deviation |
| PR | : Problem report |
| CC | : Change Control |
| QA | : Quality Assurance |
| CQA | : Corporate Quality Assurance |
| EAM | : Engineering and Maintenance |
| SOP | : Standard Operating Procedure |
| GMP | : Good Manufacturing Practices |
| BRL | Bioanalytical Research Lab |
| BAL | Bioanalytical Lab |
| HPU | Human Pharmacological unit |